## Intro and Final Outputs
IPC and IDL Climate Tools Package
Cross Ventilation Capacity Calculations
Description:
Cross ventilation can be an effective way to passively cool a building by capturing the prevailing winds during the summertime and channeling them through a space. To admit the required amount of natural ventilation into a building, the system will require a certain amount of inlets and outlets provided by operable windows or envelope-integrated louver systems. Additionally, thin plan building forms that are free from significant interior partitions will provide the ideal environment for cross ventilation. The following calculations operate under the assumption of a minimum of three degrees Fahrenheit temperature difference between the interior and exterior environment. A smaller temperature difference will potentially cause the system will start to admit hot air into the building and contribute to the heat gain rate of the space. It should be noted that these calculations can only be used to assess how much cooling capacity (or demand) the systems can contribute under the specified conditions, which can vary widely throughout the cooling season. Consequently, they should only be used as a general rule of thumb and building performance simulation should be conducted to quantify actual cooling capacities and annual energy savings.
Instructions:
This page contains the final results of the calculations of the worksheet. Start with the tab labeled "Step 1" and follow the step-by-step process using the reference tab if needed. Finish going through all tabs before returning to this page to see if the cross ventilation strategy's cooling capacity will cover all or part of the building's heat gain rate.
Cell Color Legend:
Certain cells are colored in a manner that dictates whether or not they are a user defined input, or if they automatically calculate based off of internal equation or climate specific parameters. A pink cell will require you to manually input a number, while the gold cells are self-calculating or contain predetermined values.
auto calculates | user defined
To begin this worksheet, proceed to the tab labeled "Step 1"
Final Outputs
Use the worksheet named “Heat Gain Calculations” to fill out the text field below if you do not already know your building’s heat gain rate. The cooling capacity of the designed passive system will always be analyzed next to this number to compare its capacity against the calculated demand of the building.
Building or Zone Heat Gain Rate: |  | 30.47 | Btus/hr/SF
Cross Ventilation Cooling Capacity: |  | 7.8647 | Btus/hr/SF
The chart below graphically represents the ability for cross ventilation to satisfy the heat gain rate of the building.
climate tools - Boise
climate tools - Boise

## Step 1
Step 1 - Find the Flow Rate of the System
Description:
The first step in the process involves calculating the flow rate of the system in CFM (cubic feet per minute) to understand how much air the cross ventilation strategy can deliver depending upon certain input parameters. Step 2 will involve converting that CFM into a btu/hr heat gain rate for comparison with the building's heat gain rate.
This step uses the equation:
V = (Cv) A v
where:
V = volume flow rate of air in CFM
Cv = effectiveness factor that adjusts for different wind orientations.
A = area of openable window on inlet or outlet sides (whichever is smallest)
v= velocity of wind in feet per minute (use the equation: mph x 88 = feet per minute)
Step 1 - A - Window Operability
Enter the Cv (effectiveness factor) of your building. If the windows are perpendicular to the winds use .5 -.6, if the wind is diagonal to the window opening then a .35 factor should be used. Refer to the wind rose in Figure 1 on "Reference Tab A" to determine your climate's primary wind direction for your selected season and time of day for analysis.
Cv EffectivenessFactor: |  | 0.33
Step 1 - B - Building Design
Calculate the opening of the inlet or outlet of the building, whichever is smaller as this will dictate the performance of the system. Note that the window area is not the amount of operable opening. Typically an effective opening factor can be applied to certain types of windows or this number will be available on most manufacturers’ specifications. Figure 2 on “Reference Tab A” lists some typical effective opening factors for different window types.
Area of windows (not operable opening): |  |  | 112 | SF
Area of operable opening: |  |  | 36.96 | SF
Step 1 - C - Wind Speed Calculation
Refer to Figure 3 of "Reference Tab A" to determine the average wind speed of your area. Simply take the average values of the cooling season and find their mean. Use this number for the average wind speed value for this worksheet.
Preliminary wind speed |  |  | 7.5 | mph
Once this value has been determined, it is important to note that this data likely came from an airport weather station whose surrounding area and terrain may differ greatly from your project’s site conditions. Consequently, airport wind data is often significantly higher than urban and even rural conditions. To compensate for this discrepancy, a wind speed variance factor needs to be applied to the preliminary wind speed value obtained earlier in Step 3 - A. Use Figure 4 of "Reference Tab A" to determine the correct wind speed reduction factor.
Wind Speed Reduction Factor: |  |  | 0.38
Adjusted Average Windspeed: |  |  | 3.5 | mph
The equation calls for this number to be in feet per second versus miles per hour, which can be found by multiplying the adjusted average wind speed value by 88.
Final Average Windspeed: |  |  | 308 | feet per second
Step 1 - D - Final Airflow Rate
Total CFM of Cross Ventilation System: |  |  |  |  | 3756.6144 | CFM
You may proceed to tab labelled "Step 2".
climate tools - Boise
climate tools - Boise

## Step 2
Step 2 - Convert the Flow Rate to a Cooling Capacity
Description:
The next step in the process involves taking the CFM flow rate found in step 1 and converting it into a sensible heat exchange in Btus/hr. This sensible heat exchange is contingent upon the temperature difference between the indoor and outdoor air, which we usually assume to be the minimum three degrees Fahrenheit for effective cross ventilation. This sensible heat exchange can then be converted into a cooling capacity with the square footage value of the building, which can then be compared to its heat gain rate on the "Intro and Final Outputs" tab to determine if the cross ventilation system is adequate. Keep in mind that the sensible heat exchange, and thus cooling capacity, will change with magnitude of the delta T, so this calculation only represents ONE condition of cross ventilation. More accurate consideration can be obtained through utilizing building performance software to model dynamically changing temperature differences over the entire cooling season.
This step uses the equation:
qv = (V) (1.08) (delta T)
where:
qv = sensible heat exchange due to ventilation
V = CFM rate found in Step 1
1.08 = a constant value derived from the multiplication of the density of air with the specific heat of air.
delta T = the temperature difference between outdoors and indoors
Step 2 - A - Sensible Cooling Rate
CFM obtained from Step 1: |  | 3756.6144 | CFM
delta T: |  | 3
Constant Value: |  | 1.08 | Btu-min/(CF)(h)(deg F)
Sensible Cooling Rate: |  | 12171.4307 | Btu/hr
Step 2 - B - Cooling Capacity
To find the cooling capacity, simply take the square footage of the building divided by the sensible cooling rate defined in Step 2 - A.
Building square footage: |  | 1547.6 | SF
Cross Ventilation Cooling Capacity: |  |  |  | 7.8647 | Btus/hr/SF
Return to the "Intro and Final Outputs" tab to compare the cooling capacity with the building's heat gain rate.
Step 2 - D - Auxilary Informaiton
The following chart illustrates the impact that temperature difference has on the cooling capacity of a stack ventilation system. Typically we will always use the minimum 3 degree temperature difference (as with the calculations above) to anticipate "worst case scenario" conditions, but a more acute approach can be taken dependent upon building, climate, and what month you are analyzing. In the chart below you can see the different cooling capacities based off of varying temperature differences. If the 3 degree temperature difference is not used, then it is up to the discretion of the designer to decide which value is most appropriate. Simply use the graph to find whichever cooling capacity your temperature difference will elicit, and then compare it with the heat gain rate on the "Intro and Final Outputs" tab.
The chart below references hidden cells in this spreadsheet that automatically calculate the different delta T's and cooling capacities based off of the parameters input earlier in this step.
Delta T | Cooling Capacity
3 | 7.8647
4 | 10.4863
5 | 13.1079
6 | 15.7294
7 | 18.351
8 | 20.9726
9 | 23.5941
10 | 26.2157
Deg F | Kbtu/hr/SF
climate tools - Boise
climate tools - Boise

## Reference Tab A
References
Figure 1 - Wind Roses
Source: Ecotect Weather Tool 2011
Figure 2 - Effective Opening Factors
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Canada. John Wiley & Sons. Copyright 2000
Figure 3 - Wind Speed Chart
Source: Climate Consultant 5
Figure 4 - Wind Speed Reduction
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Canada. John Wiley & Sons. Copyright 2000
frequency (hrs)
46+
Summertime Wind Rose (daytime)
Summertime Wind Rose (nighttime)
frequency (hrs)
106+
North
North
Autumn Wind Rose (daytime)
frequency (hrs)
20+
North
Autumn Wind Rose (nighttime)
frequency (hrs)
94+
North
SpringWind Rose (night time)
frequency (hrs)
94+
North
Spring Wind Rose (nighttime)
frequency (hrs)
94+
North
wind speed in MPH
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise