## Intro and Final Outputs
IPC and IDL Climate Tools Package
Heat Gain Calculations
Description:
The heat gain rate of the project is an important metric in determining how to size passive design strategies and systems. The heat gain rate of your building, often measured in Btus/hr/square foot, will determine the cooling capacity requirement of either the building’s passive or active systems. The amount of heat gain in a particular building or zone is the product of multiple factors including heat gains through the building envelope, air infiltration, ventilation, and the internal gains of a building from inhabitants and other types of equipment.
Instructions:
This page contains the final results of the calculations of the worksheet. Start with the tab labeled "Step 1" and follow the step-by-step process using the reference tab if needed. Finish going through all tabs before returning to this page to see the heat gains broken apart into their constituent loads and the resultant total heat gain rate of the building.
Cell Color Legend:
Certain cells are colored in a manner that dictates whether or not they are a user defined input, or if they automatically calculate based off of internal equation or climate specific parameters. A pink cell will require you to manually input a number, while the gold cells are self-calculating or contain predetermined values.
auto calculates |  | user defined
To find the heat gain rate of your building, proceed to the tab labelled "Step 1".
Final outputs |  | Building Area: | 1547.6 | SF
| Heat Gain Source |  | Heat Gain |  | Heat Gain Rate
| roof and walls: |  | 2298.789 | btus/hr | 1.4854 | Btus/hr - SF
| glass: |  | 15380 | btus/hr | 9.938 | Btus/hr - SF
| outdoor air: |  | 37622 | btus/hr | 24.3099 | Btus/hr - SF
| people: |  | 25148.5 | btus/hr | 16.25 | Btus/hr - SF
| lights: |  | 619 | btus/hr | 0.39997 | Btus/hr - SF
| equipment: |  | 5280 | btus/hr | 3.4117 | Btus/hr - SF
| Latent Heat Gains: |  | 8634.8289 | btus/hr | 5.5795 | Btus/hr - SF
| Total Sensible Heat gains: |  | 94983.1179 | btus/hr
| Total building heat gain rate: |  |  |  | 61.3745 | Btus/hr - SF
The chart below shows a disaggregated chart that breaks the building's heat gain rate into its constituent load factors.
climate tools - Boise
climate tools - Boise

## Step 1
Step 1: Heat Gains through Roof and Walls
Description:
The first step in the process calculates the heat gains of the opaque parts of the envelope through conduction based off of the outdoor air temperature. Each wall of the zone or building will be analyzed and calculated separately with respect to each other.
This process will use the equation:
q = U x A x DETD
where:
q = the heat gain of the wall, roof, floor, etc.
U = u value of the component assembly
A = area of the wall, roof, floor, etc.
DETD = design equilavent temperature difference
Step 1 - A - Area of Envelope
Input the area of the following components and the u value of their assemblies (Average the wall area if multiple walls in same direction exists). The floor does not account for any heat gain in the summertime.
| Area of North Wall: | 510.2 | SF | U-Value of North Wall: | 0.05
| Area of South Wall: | 1139.4 | SF | U-Value of South Wall: | 0.05
| Area of East Wall: | 478 | SF | U-Value of East Wall: | 0.05
| Area of West Wall: | 475 | SF | U-Value of West Wall: | 0.05
| Area of Roof: | 1670 | SF | U-Value of Roof: | 0.016
| Area of Floor: | 1547 | SF | U-Value of Floor: | 0
Step 1 - B - Climate Data
The following information is automatically updated to the target city and will be used to calculate the rate of heat gain through the roof and walls. Temperature statistics are referenced from ASHRAE 90.1 2007, but can be overridden to reflect any weather or climate standard.
| Design Dry Bulb |  | 94 | deg F
| Mean Daily Temperature Range |  | 31 | deg F
Step 1 - C - Design Equilavent Temperature Differences
Use the the two values found in Step A-1 in conjuction with Figure 1 in "Reference Tab A" to find the DETD of each the following components.
| DETD of North Wall: | 11.3
| DETD of South Wall: | 11.3
| DETD of East Wall: | 11.3
| DETD of West Wall: | 11.3
| DETD of Roof: | 31
| DETD of Floor: | 0
Step 1 - C - Design Equilavent Temperature Differences
The heat gain through the envelope should automatically calculate based upon the above equation and the input parameters defined in steps 2 A-C.
| Heat Gain of North Wall: | 288.263 | Btus/hr
| Heat Gain of South Wall: | 643.761 | Btus/hr
| Heat Gain of East Wall: | 270.07 | Btus/hr
| Heat Gain of West Wall: | 268.375 | Btus/hr
| Heat Gain of Roof: | 828.32 | Btus/hr
| Heat Gain of Floor: | 0 | Btus/hr
| Total Heat Gains: | 2298.789 | Btus/hr
You may now proceed to the tab labeled "Step 2".
climate tools - Boise
climate tools - Boise

## Step 2
Step 2: Heat Gains Through Glass
Description:
The next step in the process calculates the heat gains of the transparent parts of the envelope through both conduction and solar heat gain admittance. Each orientation of glazing (both horizontal and vertical) will be analyzed and calculated separately with respect to each other.
This process will use the equation:
q = A x DCLF
where:
q = heat gain from windows
A = the area of the windows
DCLF = design cooling load factors
Step 2-A - Glass Area
Input the area of the following components
Area of North Window: |  | 112 | SF | of Northwest Window: |  | SF
Area of South Window |  | 431 | SF | of Northeast Window: |  | SF
Area of East Window: |  | 140 | SF | of Southwest Window: |  | SF
Area of West Window: |  | 140 | SF | of Southeast Window: |  | SF
Area of skylights: |  |  | SF
Step 2-B - Design Cooling Load Factors
Refer to the Figure 2 in the tab labeled "Reference A" to find the design cooling load factors for each glazing orientation based off window type.
DCLF of North Window: |  | 17 |  | of Northwest Window:
DCLF of South Window |  | 16 |  | of Northeast Window:
DCLFof East Window: |  | 0 |  | of Southwest Window:
DCLF of West Window: |  | 47 |  | of Southeast Window:
DCLF of skylights:
Step 2-C - Heat Gain Calculations
The heat gain through the window orientations should automatically calculate based upon the above equation and the input parameters defined in steps 2 A-C.
Heat Gain of North Window: |  | 1904 | Btus/hr | of Northwest Window: | 0 | Btus/hr
Heat Gain of South Window |  | 6896 | Btus/hr | of Northeast Window: | 0 | Btus/hr
Heat Gain of East Window: |  | 0 | Btus/hr | of Southwest Window: | 0 | Btus/hr
Heat Gain of West Window: |  | 6580 | Btus/hr | of Southeast Window: | 0 | Btus/hr
Heat Gain of skylights: |  | 0 | Btus/hr
| Total Heat Gains: |  | 15380 | Btus/hr
You may now proceed to the tab labeled "Step 3".
climate tools - Boise
climate tools - Boise

## Step 3
Step 3: Heat Gains from the Outdoor Air
Description:
Sensible heat gain from outdoor air is a factor of both infiltration and the amount of airflow the ventilation system introduces into the building. The amount of outdoor air depends on number of people and the activity type of the building. For commercial buildings, use OPTION 1; for residential buildings, use OPTION 2. Be sure to manually input the final heat gains from outdoor air from whichever option is used to calculate Step 3.
OPTION 1 - Commercial Buildings
Commercial buildings primarily incur a peak cooling load from outdoor air introduced into the building by a mechanical ventilation system. During occupied times, the building is assumed to be positively pressurized and thus negates most significant heat gains from infiltraiton.
The process uses the equation:
q (ventilation) = Q x V
where:
q = heat gain from ventilation
Q = volume of the outdoor air (total cfm orL/s)
V = ventilation factor
OPT 1 - Step 3 - A - Calculate the Number of Occupants
The volume of airflow required is based off of the number of people in the space and the type of building. This can be estimated using Figure 3 in "Reference Tab A" which references typical code occupancies that are based off of floor area. OR you can just override the equation and input the actual amount of people in the "Number of People" field.
| Building Floor Area: |  | 1547.6 | SF
| Building Floor Area in Thousandths: |  | 1.5476
| People per 1000 square feet (Figure 3): |  | 65 | SF/person
| Number of People: |  | 100.594 | people
OPT 1 - Step 3 - B - Calculate the Ventilation Rate
Refer to Figure 4 in "Reference Tab A" to find the recommended outdoor air requirement for the ventilation of your type of building.
| CFM per person: |  | 17 | CFM/person
| Total CFM of Volume of Outdoor Air = |  | 1710.098 | CFM
OPT 1 - Step 3-C - Calculate the Ventilation Factor
The ventilation factor is based off of the design temperature of the climate (refer to Step 1 - B) and Figure 5 in "Reference Tab A". This value represents the heat gain contribution of the air admitted into the building through mechanical ventilation based on CFM.
| Ventilation Factor: |  | 22 | Btu/hr/SF
| OPT 1 - Total Heat Gains |  | 37622.156 | Btus/hr
OPTION 2 - Residential Buildings
In residences, outdoor air is not introduced into the building through a mechanical system. Rather, outdoor air's contribution to the peak cooling load of a home is typically the result of infiltration through the envelope.
The process uses the equation:
q (infiltration) = EA x I
where:
q = heat gain from infiltration
EA = square footage of area of envelope exposed to the outside
I = infiltration factor
OPT 2 - Step 3 - A - Calculate the Exposed Area of the Building
Infiltration is based off of an infiltration factor applied to the amount of exposed area of the building. First, combine the area from any walls (including window area) and roofs that are exposed to the outdoor environment.
Area of Exposed Walls: |  |  | SF
Area of Exposed Roof |  |  | SF
Total Exposed Area |  | 0 | SF
OPT 2 - Step 3 -B - Infiltration Factor
The infiltration factor is based off of the design temperature of the climate (refer to Step 1 - B) and Figure 5 in "Reference Tab A". This value represents the heat gain contribution of the air admitted into the building through infiltration ventilation based off square footage.
Infiltration Factor |  |  | Btus/hr- SF
| OPT 2 - Total Heat Gains |  | 0 | Btus/hr
Final Step
Enter the total heat gain from either Option 1 or Option 2 in the field below:
| Total Heat Gains |  | 37622
You may now proceed to the tab labeled "Step 4".
climate tools - Boise
climate tools - Boise

## Step 4
Step 4: Heat Gains from People
Description:
Depending on the building type and activity level, the internal heat gains from people can be a significant factor in the overall heat gain rate. The human body acts as a heat source that must be considered in any building design.
The process uses the equation:
q = O x SHGO
Where:
q = sensible heat gain from people
O = number of occupants
SHGO = sensible heat gain per occupant
Step 4-A - Calculate the Number of Occupants
Refers to Step 3 - A
| Number of Occupants: | 100.594 | people
Step 4-B - Calculate the Sensible Heat Gain Per Occupant
Determine the activity level of the occupants based on building type and refer to Figure 6 to find the sensible heat gain per occupant.
| SHGO: | 250 | Btu/hr
| Total Heat Gains | 25148.5 | Btus/hr
You may now proceed to the tab labeled "Step 5".
climate tools - Boise

## Step 5
Step 5: Heat Gains from Lights
Description:
Calculating the heat gain from the electrical lighting system can take one of two different pathways. Option 1 uses a standard equation that factors in the heat gain rate associated with the lighting power density of the lights and ballasts. Option 2 should be used if daylighting is going to play a factor in the space and affect the electrical lighting operation. This option calculates a heat gain rate based off of the daylight factor of the building and reduced electrical lighting operation based off of a photocontrolled dimming system with an 80% dimming factor
OPTION 1 - Standard Calculation
This process uses the equation:
q = LPD x SF x Btu factor
where:
LPD = lighting power density
SF = space square footage
Btu Factor = multiply by 3.412 to get watts into Btus
OPT 1 - Step 5 - A - Lighting Power Density Calculation
Refer to the Ashrae tables listed as Figure 7 in "Reference Tab A" to find the building type's maximum power density. Use either the "building area" approach or "space-by-space" approach.
| Building Square Footage: | 1547.6 | SF
| Lighting Power Density: | 1.1 | watts/SF
| Btu Factor: | 3.412 | Btus
| Lighting Heat Gains: | 5808.4523 | Btus/hr
OPT 1 - Step 5 - B - Lighting Ballast Heat Gain
The ballasts of the light fixture also contribute to the heat gain of this step. To account for this factor, multiply the lighting heat gains by either 1.12 for energy efficient ballasts, or 1.2 for normal ballasts, OR you can enter in a specific product performance factor form spec sheets or manufacturer information.
| Ballast Factor: | 1.12
| Opt 1 Total Heat Gains | 6505.4666 | Btus/hr
OPTION 2 - Daylight Factored Calculation
This process uses an electric lighting heat gain rate that is contingent upon a daylight factor of the building. Consequently, the daylight factor must first be calculated based upon the area of windows of both sidelighting and toplighting strategies.
OPT 2 - Step 5 - A - Sidelighting Daylight Factor Calculation
This process uses the equation below. For multiple floors or different rooms, average all the constituent daylight factors together and override the "Daylight Factor from Sidelighting" field:
DF = .2 x (window area/floor area)
| Building Floor Area: | 1547.6 | SF
| Window Area: | 793 | SF
| Daylight Factor from Sidelighting: | 10.25% | %
OPT 2 - Step 5 - B - Toplighting Daylight Factor Calculation
The toplighting equation is similar to the sidelighting equation, but the factors vary depending on the geometry of the skylight. For multiple floors or different rooms, average all the constituent daylight factors together and override the "Daylight Factor from Toplighting" field:
toplighting factor:
use .2 for vertical monitors, use .33 for north-facing sawtooths, and use .5 for horizontal skylights.
| Skylight Area: |  | SF
| Daylight Factor from Toplighting: | 0% | %
To calculate the total daylight factor, add the two total daylight factor percentages together:
| Total Daylight Factor: | 10.25% | %
OPT 2 - Step 5 - C - Calculating Internal Heat Gain
Use the total daylight factor found in OPT2- Step 5 - B and Figure 8 to input the sensible heat gain. This rate multiplied by the building's area will yield the total heat gain contribution of a daylighting controlled electric lighting system combination.
| Sensible Heat Gain Rate (Fig 8): | 0.4
| Opt 2 Total Heat Gains | 619.04 | Btus/hr
Final Step
Enter the total heat gain from either option 1 or 2 in the field below:
| Total Heat Gains | 619 | Btus/hr
You may now proceed to the tab labeled "Step 6".
climate tools - Boise
climate tools - Boise
climate tools - Boise

## Step 6
Step 6: Heat Gains from Equipment
Description:
There are two different ways to calculate the contribution of electrical equipment to the heat gain rate of the building. Option one involves taking an inventory of all pieces of equipment used in the building and adding together their watts or sensible heat gain. The other option uses a standard equation based off of the code maximum equipment power density to calculate heat gain. If the number of total watts can be gathered, this value can be multiplied by a factor of 3.413 to convert to a heat gain metric.
OPTION 1 - Inventory Method
Take inventory of all the pieces of electrical equipment in your building. Next, use Figure 9 in "Reference Tab A" to calculate and total the amount of watts (not the "recommended rate of heat gain") that each piece of equipment uses. OR you may also look online for a specific brand's power ratting and wattage output, which will reflect the most recent efficiency advancements in current product development.
Total watts: |  | 1547.6 | watts
Btu/hr conversion factor: |  | 3.412 | Btus/hr
Opt 1 Total Heat Gains |  | 5280.4112 | Btus/hr
OPTION 2 - Standard Equation Method
This process uses the equation:
q = EPD x SF x 3.412 Btus/hr
Where:
q = heat gain from equipment
EPD = equipment power denisty
SF = square footage of the building
3.412 = watts to Btu/hr conversion
Option 2 - Step A
Use Figure 10 in "Reference Tab A" to find the proper equipment power density of your building according to type.
Building Area: |  | 1547.6 | SF
Equipment Power Density: |  | 0.9 | watts/SF
Opt 2 Total Heat Gains |  | 4752.3701 | Btus/hr
Final Step
Enter the total heat gain from either option 1 or 2 in the field below:
| Total Heat Gains |  | 5280 | Btus/hr
You may now proceed to the tab labeled "Step 6".
climate tools - Boise
climate tools - Boise

## Step 7
Step 7: Latent Heat Gains
Description:
Latent heat gains vary with the type of occupancy of a building, but can be estimated based upon outdoor air infiltration and climate design temperatures. This method estimates additional latent heat gain as a percentage of the total sensible heat gains found in Steps 1-6. The design dry bulb temperature and mean coincident wet bulb temperature, along with the relative tightness of building construction, determine the latent percentage of total sensible heat gain.
Step 7 - A - Climate Information
The design dry bulb temperature and wet bulb temperature for the city that your project resides within play an important role in determining the latent heat gain.
Design Dry Bulb Temperature: |  | 94 | deg F
Wet Coincident Wet Bulb Temperature: |  | 64 | deg F
Step 7 - B- Percentage Calculation
Use these two values to navigate Figure 11, along with an assumption about the relative tightness of construction, to find the percentage of latent heat gain.
Percentage of Latent Heat Gain: |  | 0.1 | (input in decimal format)
Total Sensible Heat Gain of Steps 1-6: |  | 86348.289 | Btus/hr
| Total Heat Gains: | 8634.8289 | Btus/hr
You may now refer back to the "Intro and Final Outputs" tab for comparison.
climate tools - Boise

## Reference A
References
Figure 1 - Design Equivalent Temperature Differences (DETD)
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Start at the left of the graph with the type of assembly before moving right along its axis to find the DETD that lies under both the outdoor design temperature and daily temperature range of your project. Above 30 is considered high, in between 15-30 is medium, and anything below 15 is low.
Figure 2 - Design Cooling Load Factors Through Glass
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Start with the orientation of the glass on the left side of the chart before moving vertically to find the correct shading segment, moving then horizontally to find the correct glass type segment, before moving again horizontally to correspond to the outdoor design temperature.
Figure 3 - Code Occupancy Requirements - ASHRAE 90.1
Source: ASHRAE 90.1-2007. "Energy Standard for Buildings Except Low-Rise Residential Buildings". Atlanta, Georgia, 2007.
Occupancy Category |  | Occupant Density per 1000 ft |  | Occupant Density per 1000 ft
Correctional Facilities |  |  | Misc Spaces
cell |  | 25 | bank vaults | 50
day room |  | 30 | computer (not printing) | 4
guard stations |  | 15 | pharmacy | 10
booking/waiting |  | 50 | photo studios | 10
Educational Facilities |  |  | shipping/receiving | -
daycare |  | 25 | transportation waiting | 100
classrooms (ages 5-8) |  | 25 | warehouses | -
classrooms (age 9 +) |  | 35 | Public Assembly Spaces
lecture classroom |  | 65 | auditorium seating area | 150
lecture hall (fixed seats) |  | 150 | places of worship | 120
art classroom |  | 20 | courtrooms | 70
science laboratories |  | 258 | legislative chambers | 50
wood/metal shop |  | 20 | libraries | 10
computer lab |  | 25 | lobbies | 150
media center |  | 25 | museums (childrens) | 40
music/theater/dance |  | 35 | meseums/galleries | 40
multi-use assembly |  | 100 | Retail
Food Service |  |  | Sales | 15
restaurant dining rooms |  | 70 | mall common areas | 40
cafeteria |  | 100 | Barber shop | 25
bars, cocktail lounges |  | 100 | beauty and nail salons | 25
General |  |  | pet shops | 10
conference/meeting |  | 50 | supermarket | 8
corridors |  | - | coin-operated laundries | 20
storage rooms |  | - | Sports and Entertainment
Hotels, Dorms |  |  | sports arena | -
bedroom/living room |  | 10 | gym, stadium | 30
barracks sleeping areas |  | 20 | spectator areas | 150
lobbies/prefunction |  | 30 | swimming pool | -
multipurpose assembly |  | 120 | dance floors | 100
Office Buildings |  |  | aerobics room | 40
office space |  | 5 | weight room | 10
reception areas |  | 30 | bowling alley (seating) | 40
telephone/data entry |  | 60 | casinos | 120
main entry lobbies |  | 10 | arcades | 20
|  |  | stages/studios | 70
Figure 4 - Ventilation Rates by Space Type
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Occupancy Category |  | cfm/person |  | cfm/person
Correctional Facilities |  |  | Misc Spaces
cell |  | 10 | bank vaults | 17
day room |  | 7 | computer (not printing) | 20
guard stations |  | 9 | pharmacy | 23
booking/waiting |  | 9 | photo studios | 17
Educational Facilities |  |  | shipping/receiving | -
daycare |  | 17 | transportation waiting | 8
classrooms (ages 5-8) |  | 15 | warehouses | -
classrooms (age 9 +) |  | 13 | Public Assembly Spaces
lecture classroom |  | 8 | auditorium seating area | 5
lecture hall (fixed seats) |  | 8 | places of worship | 6
art classroom |  | 19 | courtrooms | 6
science laboratories |  | 17 | legislative chambers | 6
wood/metal shop |  | 19 | libraries | 17
computer lab |  | 15 | lobbies | 5
media center |  | 15 | museums (childrens) | 11
music/theater/dance |  | 12 | meseums/galleries | 9
multi-use assembly |  | 8 | Retail
Food Service |  |  | Sales | 16
restaurant dining rooms |  | 10 | mall common areas | 9
cafeteria |  | 9 | arber shop | 10
bars, cocktail lounges |  | 9 | beauty and nail salons | 25
General |  |  | pet shops | 26
conference/meeting |  | 6 | supermarket | 15
corridors |  | - | coin-operated laundries | 11
storage rooms |  | - | Sports and Entertainment
Hotels, Dorms |  |  | spors arena | -
bedroom/living room |  | 11 | gym, stadium | -
barracks sleeping areas |  | 8 | spectator areas | 8
lobbies/prefunction |  | 10 | swimming pool | -
multipurpose assembly |  | 6 | dance floors | 21
Office Buildings |  |  | aerobics room | 22
office space |  | 17 | weight room | 26
reception areas |  | 7 | bowling alley (seating) | 13
telephone/data entry |  | 6 | casinos | 9
main entry lobbies |  | 11 | arcades | 17
|  |  | stages/studios | 11
Figure 5 - Infiltration and Ventilation Factors
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Be sure to use either the appropriate infiltration factor or ventilation factor in the worksheet.
Figure 6 - Heat Gain Rate from Occupants
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Be sure to use the "sensible" heat gain column". The latent heat gain is not a factor in this step because the total latent heat gains are covered in step 7.
Figure 7- Lighting Power Density References
Source: ASHRAE 90.1-2007. "Energy Standard for Buildings Except Low-Rise Residential Buildings". Atlanta, Georgia, 2007.
Building Area Method
Space by Space Method
Figure 8 - Heat Gain Through Lights Based on Daylight Factor
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Figure 8 - Heat Gain Through Lights Based on Daylight Factor
Source: G.Z. Brown and Mark DeKay. "Sun, Wind & Light." New York, John Wiley & Sons, Inc. 2001
The "lo" and "hi" columns represent the range specified in old ASHRAE specifications. For our calculation, use the "lo" column if using the minimum LPD requirements of the zones space type.
Boise Latitude: | 43 degrees
Figure 9- Heat Gain Through Electrical Equipment
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Figure 10 - Equipment Power Densities
Source: ASHRAE 90.1-2007. "Energy Standard for Buildings Except Low-Rise Residential Buildings". Atlanta, Georgia, 2007.
The "receptical power density" column represents the equipment power density used in the worksheet.
Figure 11 - Latent Heat Gain Factor
Source: Reynolds, Stein. "Mechanical and Electrical Equipment for Buildings" Tenth Edition. Canada. John Wiley & Sons. Copyright 2006
Start with the dry bulb design temperature at the bottom axis of the graph, next move up until the correct wet bulb line is intersected. Last, move to the right and identify which construction type your project falls under and record the percentage value, which represents the amount of latent heat gain based off of the total sensible heat gain. If your values fall below the dotted lines, assume a minimum 10%.
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise
climate tools - Boise