## Intro and Final Outputs
IPC and IDL Climate Tools Package
Stack Ventilation Capacity Calculations
Description:
Stack ventilation can be an effective method of natural ventilation when cross ventilation is not available. Stack ventilation relies on the buoyancy, pressure differentials, and fluid dynamic properties of air to drive ventilation throughout a building. For example, as heat transfers through the medium of air, warmed air rises and can be exhausted while it pulls in cooler air through lower openings. This particular method is useful when site, building, or climate constraints limit the amount of wind and effectiveness of cross ventilation. Stack ventilation’s performance will be dependent on the smaller of the following parameters: inlet size, outlet size, and stack throat area (i.e. the shaft opening area of a tower or chimney). As with cross ventilation, the following calculations operate under the assumption of a minimum three degrees Fahrenheit temperature difference between the interior and exterior environment. A smaller amount of temperature difference will potentially cause the system will start to admit hot air into the building and contribute to the heat gain rate of the space. These calculations can only be used to assess how much cooling capacity (or demand) the systems can contribute under the specified conditions, which can vary widely with actual weather inputs over the cooling season. Consequently, they should only be used as a general rule of thumb and building performance simulation should be conducted to quantify actual cooling capacities and annual energy savings.
Also note that stack ventilation can be driven by cross ventilation, thereby increasing the amount of airflow and cooling capacity of the system. If your building proposes to use both, be sure to fill out step 3 as well as the rest of this worksheet.
Instructions:
This page contains the final results of the calculations of the worksheet. Start with the tab labeled "Step 1" and follow the step-by-step process using the reference tab if needed. Finish going through all tabs before returning to this page to see if the stack ventilation strategy's cooling capacity will cover all or part of the building's heat gain rate.
Cell Color Legend:
Certain cells are colored in a manner that dictates whether or not they are a user defined input, or if they automatically calculate based off of internal equation or climate specific parameters. A pink cell will require you to manually input a number, while the gold cells are self-calculating or contain predetermined values.
auto calculates | user defined
To begin this worksheet, proceed to the tab labeled "Step 1"
Final Outputs
Use the worksheet named “Heat Gain Calculations” if you do not already have a heat gain rate. This number will always be compared against the cooling capacity of the system calculated throughout this worksheet to analyze the ability of the system to meet the cooling demand of the building.
Building or Zone Heat Gain Rate: |  | 30.47 | Btus/hr/SF
Stack Ventilation Cooling Capacity: |  | 4.8796 | Btus/hr/SF
Combined Stack and Cross Ventilation Cooling (if applicable) |  | 9.2536 | Btus/hr/SF
The chart below graphically represents the ability for stack ventilation to satisfy the heat gain rate of the building.
climate tools - Boise
climate tools - Boise

## Step 1
Step 1 - Find the Flow Rate of the System
Description:
The first step in the process involves calculating the flow rate of the system in CFM (cubic feet per minute) to understand how much air the stack ventilation strategy can deliver depending upon certain input parameters. Step 2 will involve converting that CFM into a Btu/hr heat gain rate for comparison with the building's heat gain rate.
This step uses the equation:
V = 60KA gh(Ti - To)/Ti
where:
V = volume flow rate of air in CFM
K = discharge coefficient for openings (assume .65 for multiple inlets)
A = in square feet, the smaller of either the total area of the inlets or outlets or horizontal cross-sectional area (throat area) of the stack
g = gravitational constant, 32.2 ft/s2
h= stack height
Ti = temperature indoors in degrees Rankine (deg R)
To = temperature outdoors in degrees Rankine (deg R)
Step 1 - A
Calculate the area of the smaller of the inlet area, outlet area, or stack throat area, as the lowest value will dictate the performance of the system.
Smallest area of inlet, outlet or stack throat: |  | 71.28 | square feet
Step 1 - B
Calculate the height of the stack. This value is the distance between the bottom of the inlet and the top of the outlet.
stack height: |  | 15.8 | feet
Step 1 - C
To calculate the temperature differences, we have to make some assumptions about indoor and outdoor temperature. Keeping in mind that our minimum temperature difference should be three degrees, we can use this to determine our indoor and outdoor performance parameters. A common indoor temperature value would be the cooling setpoint of the HVAC system (75 deg F)
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 70 | deg F
|  | 529.67 | deg R
Total CFM of Stack Ventilation System: |  |  | 2330.7812 | CFM
You may now proceed to tab labelled "Step 2".
Step 1 - D - Auxilary Informaiton
The following chart illustrates the impact that the temperature difference has on the air flow rate of a stack ventilation system. Typically we will always use a 3 degree temperature difference (as with the calculations above) to anticipate "worst case scenario" conditions, but a more acute approach can be taken dependent upon building, climate, and what month you are analyzing. Additionally, if stack ventilation is evaluated under a night flush ventilation scenario, a larger delta T can be used to represent the cooler outdoor temperatures of nightfall. Typically, 5 deg F can be assumed for minimum requirements and "worst case scenario" conditions.
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 72 | deg F
|  | 531.67 | deg R
|  | 3 | 1398.4687
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 71 | deg F
|  | 530.67 | deg R
|  | 4 | 1864.625
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 70 | deg F
|  | 529.67 | deg R
|  | 5 | 2330.7812
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 69 | deg F
|  | 528.67 | deg R
2796.9375
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 68 | deg F
|  | 527.67 | deg R
|  | 7 | 3263.0937
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 67 | deg F
|  | 526.67 | deg R
|  | 8 | 3729.2499
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 66 | deg F
|  | 525.67 | deg R
|  | 9 | 4195.4062
Indoor temperature: |  | 75 | deg F
|  | 534.67 | deg R
Outdoor temperature: |  | 65 | deg F
|  | 524.67 | deg R
|  | 10 | 4661.5624
The chart below references hidden cells in this spreadsheet that automatically calculate the different delta T's based off of the parameters input earlier in this step.
Delta T | Airflow
3 | 1398.4687
4 | 1864.625
5 | 2330.7812
6 | 2796.9375
7 | 3263.0937
8 | 3729.2499
9 | 4195.4062
10 | 4661.5624
deg F | CFM
climate tools - Boise
climate tools - Boise

## Step 2
Step 2 - Convert the Flow Rate to a Cooling Capacity
Description:
The next step in the process involves taking the CFM flow rate found in step 1, and converting it into a sensible heat exchange in Btus/hr (cooling effect). Like the air flow rate for stack ventilation, the system’s sensible heat exchange is also contingent upon the temperature difference between the indoor and outdoor air, which we usually assume to be the minimum three degrees Fahrenheit for effective stack ventilation. This sensible heat exchange can then be converted into a cooling capacity using the square footage value of the building. This value can then be compared to its heat gain rate on the "Intro and Final Outputs" tab to determine if the stack ventilation system is adequate. Keep in mind that the sensible heat exchange, and thus cooling capacity, will change with magnitude of the delta T, so this calculation only represents ONE condition of cross ventilation. More accurate consideration can be obtained through utilizing building performance software to model dynamically changing temperature differences.
This step uses the equation:
qv = (V) (1.08) (delta T)
where:
qv = sensible heat exchange due to ventilation
V = CFM rate found in Step 1
1.08 = a constant value derived from the multiplication of the density of air with the specific heat of air.
delta T = the temperature difference between outdoosr and indoors
Step 2 - A
CFM obtained from Step 1: |  |  | 2330.7812 | CFM
delta T: |  |  | 3 | Deg F
Constant Value: |  |  | 1.08
Sensible Cooling Rate: |  |  | 7551.7311 | Btus/hr
Step 2 - B
To find the cooling capacity, simply take the square footage of the building divided by the sensible cooling rate defined in Step 2 - A.
Building square footage: |  |  | 1547.6 | SF
Stack Ventilation Cooling Capacity: |  |  |  |  | 4.8796 | Btus/hr/SF
Return to the tab "intro and Final Outputs" to compare the cooling capacity with the building's heat gain rate OR proceede to tab "Step 3".
Step 2 - D - Auxilary Informaiton
The following chart illustrates the impact that the temperature difference has on both the air flow rate and cooling capacity of a stack ventilation system. Typically we will always use a 3 degree temperature difference (as with the calculations above) to anticipate "worst case scenario" conditions, but a more acute approach can be taken dependent upon building, climate, and what month you are analyzing. Here you can see the different cooling capacities and flow rates based off of varying temperature differences. If the 3 degree temperature difference is not used, then it is up to the discretion of the designer to decide which value is most appropriate. Simply use the graph to find whichever cooling capacity your temperature difference will elicit, and then compare it with the heat gain rate on the "Intro and Final Outputs" tab.
The chart below references hidden cells in this spreadsheet that automatically calculate the different delta T's and cooling capacities based off of the parameters input earlier in this step.
Delta T | Airflow | Cooling Capacity
3 | 1398.4687 | 2.9278
4 | 1864.625 | 5.2049
5 | 2330.7812 | 8.1327
6 | 2796.9375 | 11.7111
7 | 3263.0937 | 15.9402
8 | 3729.2499 | 20.8198
9 | 4195.4062 | 26.3501
10 | 4661.5624 | 32.5309
deg F | CFM | Btus/hr - SF
climate tools - Boise
climate tools - Boise

## Step 3
Step 3 - Combined Stack and Cross Ventilation (OPTIONAL)
Description:
If your building does not incorporate both strategies, skip this step. In the case of buildings that utilize both cross and stack ventilation, the two system's interaction can be accounted for with the equation below. Typically the addition of cross ventilation will drive the stack effect and therefore will increase the airflow rate and the overall cooling capacity of the design.
This step uses the equation:
V = (cfm from cross ventilation) + cfm from stack
ventilation)
where:
V = total combined airflow in CFM
Step 3 - A
Input the CFM from cross ventilation (refer to the cross ventilation worksheet. Be sure to adjust your CFM if you are trying to evaluate a different temperature difference.
Cross Ventilation CFM: |  | 3756 | CFM
Input the CFM from stack ventilation (refer to step 1-c). Be sure to adjust your CFM if you are trying to evaluate a different temperature difference.
Stack Ventilation CFM: |  | 2330 | CFM
Combined Airflow Rate |  |  | 4420.0041 | CFM
Step 3 - B
Use the CFM obtained in step 3-A to find the sensible cooling rate of the combined systems.
This step uses the same equation as tab "Step 2":
qv = (V) (1.08) (delta T)
where:
qv = sensible heat exchange due to ventilation
V = CFM rate found in Step 3 - A
1.08 = a constant value derived from the multiplication of the density of air with the specific heat of air.
delta T = the temperature difference between outdoosr and indoors
Combined CFM rate: |  | 4420.0041 | CFM
delta T: |  | 3 | deg F
(make sure you use the same delta T used to find the CFM and sensible cooling rates of the stack effect found in tab "Step 2")
Sensible Cooling Rate: |  | 14320.8132 | Btus/hr
Building square footage: |  | 1547.6 | SF
Combined Cross and Stack Ventilation Cooling Capacity: |  |  |  |  | 9.2536 | Btus/hr/SF
Return to the tab "intro and Final Outputs" to compare this cooling capacity with the building's heat gain rate.
2
2
climate tools - Boise
climate tools - Boise